ARCHITECT & ENGINEER SPECIFICATIONS

SECTION  16780

VIDEO SURVEILLANCE SYSTEM

SSC-C104

General Purpose 1/3” Color CCD Camera

PART 2	PRODUCTS

2.01	CCTV CAMERA SPECIFICATIONS

A.	VIDEO - GENERAL REQUIREMENTS

1.	The camera shall utilize a 1/3" Hyper HAD7  Interline Transfer CCD image sensor.  The image sensing area shall be 4.4 mm x 3.3 mm utilizing 510h x 492v active picture elements. The camera shall produce 330 lines horizontal resolution.

2.	The camera shall require a  minimum scene illumination of 1.0 lux at f/1.2,  89.9 percent  reflectance, Turbo AGCJ ON.  To achieve full video,  the scene illumination shall be 4.5 lux at f/1.2,  89.9 percent  reflectance, Turbo AGCJ ON.

3.	The camera shall have switchable  (On/Off) automatic backlight compensation (BLC).  BLC shall function independently of object positioning and shall require no set up or programming . ( DC type auto iris lens or CCD IrisJ mode only)  The amount of BLC shall be adjustable via a potentiometer on the rear of the camera.

4.	The camera shall have switch selectable (On/Off), continuously variable CCD IrisJ with a control range of 1/60th  to  1/100,000th  second.

5.	The camera shall accept both Video (ALC) or DC (Non-ALC) auto iris lenses. This shall be accomplished through an externally accessible slide switch.

B.	VIDEO - ELECTRICAL REQUIREMENTS

1.	Input voltage shall be AC 24 volts + 10 percent ,  60 Hz,  via screw terminals.  Power consumption shall be 3.5 watts.   The camera shall be electrically isolated from input power via isolation transformer in the DC to DC converter.

2.	The scanning system shall be 525 lines,  60 fields/30 frames,  2:1 interlace.

3.	The camera shall have Auto Tracking White with an automatic adjustment range from 2,000 degrees K to 10,000 degrees K.

4.	The camera shall exhibit no geometric distortion.

5.	Camera synchronization  shall be External AC line lock with vertical phase adjustable to  + 90 degrees.

6.	The camera shall have switchable (on/off)  Automatic Gain Control (AGC).

7.	The camera shall provide switchable (Normal/Turbo) Turbo AGCTM  which shall allow for an additional 4db gain.

8.	The composite video output shall be 1.0  volt  peak to peak  @ 75 Ohms,  sync negative via a BNC connector.

9.	The signal to noise ratio shall be 52 db, weight ON

C.	MECHANICAL REQUIREMENTS

1.	Lens mount shall be C or CS.  The camera shall utilize a precision double cam mechanism to accommodate the back focal length differences without  need for an 5 mm extension ring.  Fine focus shall be accomplished via an adjustment ring for image sensor  back focus with a lock down screw.

2.	Top or bottom camera mounting shall be obtained utilizing a removable plate with 1/4" x 20 mounting holes provided.  The plate height shall be 3/8  inch ( 9 mm )

3.	The camera dimensions shall be 2 7/8"w x 2 1/4"h x 5 1/8"d  (70 x 57 x 130 mm) and weigh 1 lb. 2 oz. (550 grams)

4.	Power input terminals shall be via 2 M3 screws on the rear of the camera.

D.	ENVIRONMENTAL REQUIREMENTS

1.	The operating temperature shall be 14 degrees  F  to 122 degrees  F  (-10 degrees C to +50 degrees C).  Operating humidity shall be 20 percent  to 80 percent ,  non-condensing.

2.	The camera will be suitable for indoor applications,  or outdoor applications with an approved environmentally rated camera enclosure.

E.	REFERENCES

1.	UL Listed 1492

2.	FCC Verified  Class B Digital Device

SSCC104.2

4/96

81996 Sony Electronic Inc.  All rights reserved.  Feature and specifications subject to change without notice.  Non-metric weights and measurements are approximate. SONY, HyperHAD, CCD Iris, Smart Control and Nothing Escapes Us are trademarks of Sony.