ARCHITECT & ENGINEER SPECIFICATIONS

SECTION  16780

VIDEO SURVEILLANCE SYSTEMS

Model: SSC-C370/374

High Resolution !/2” Color Camera

PART 2  PRODUCTS

2.01 CCTV CAMERA SPECIFICATIONS

A. VIDEO - GENERAL

1.   The camera shall utilize a  high resolution  1/2" Hyper HAD   Interline Transfer CCD image sensor.               The image sensing area shall be  6.3 mm x 4.7 mm utilizing 768h x 494v active picture elements. The              camera shall produce 470 lines horizontal  resolution.

2.   The camera shall require a  minimum scene illumination of 2.5 lux at f/1.2,  89.9 percent reflectance.              To achieve full video,   the scene illumination shall be 13.4 lux at f/1.2,  89.9 percent reflectance.

3.   The camera shall have a continuously variable CCD Iris  with a control range of 1/60th  to  1/100,000th  second.

4.   The camera shall have 8 selectable shutter speeds from 1/60th  to  1/10,000th  second.

5.   The camera shall accept Video (ALC) type auto iris lenses.

B. VIDEO - ELECTRICAL REQUIREMENTS

1.   (SSC-C370)

The input voltage  shall be DC 12 volts via screw  terminals,  or DC multiplex power over coax of 24           volts + 5 volts via the optional YS-W150 or YS-W250 camera adapters.  Power consumption shall be           2.8 watts DC 12 volts and 4.0 watts with the camera adapters.  The camera shall have an external ON/OFF power switch.  However,  camera power control (on/off) shall be accomplished through  the power switch of  the camera adapters regardless of  the external on/off switch setting on the camera when used with the          YS-W150/250 power adapters only.

1.   (SSC-C374)

Input voltage  shall be AC 24 volts + 10 percent,  60 Hz,  via screw terminals.  Power consumption shall           be 4.9 watts.  The camera shall have an external power ON/OFF switch located on the rear of the camera.  The camera shall be electrically isolated from input power via isolation transformer in the DC to DC converter.

2.   The scanning system shall be 525 lines,  60 fields/30 frames,  2:1 interlace.

3.   The camera shall have through the lens, lockable Auto White Balance (AWB)  with power loss memory  retention, or continuous Auto Tracking White  (ATW),  switchable.

4.   The ATW and AWB color temperature range shall be from 2,000 degrees K to 10,000 degrees K.

5.   The camera  shall have no geometric distortion.

6.   (SSC-C370)

Camera synchronization  shall be internal or external.  External sync shall be automatic switchover upon           sensing an external synchronizing signal.  Camera shall accept Composite Sync ( 4 volts  peak to peak),            VS (1 volt peak to peak) or VBS (1 volt peak to peak) external synchronization and shall have a           horizontal phase adjustment range of + 8 sec.  The camera shall be capable of accepting external sync           over coax (VS) via the optional power adaptors YS-W150 or YS-W250.

6.    (SSC-C374)

Camera synchronization shall be switchable Internal or External AC line lock with vertical phase adjustment via push button switches in + 60 degrees  increments.

7.   The camera shall have switchable (on/off)  Automatic Gain Control (AGC).

8.   (SSC-C370)

The video output  shall be 1.0  volt  peak to peak @ 75 Ohms,  sync negative.  This output shall be           obtained on the following Mode Select setting on the camera:

a. MODE A (with YS-W150/250)  -  MONITOR OUT/VS IN  BNC Connector  Video out 1 or 2 of          YS-W150/250

b. MODE B  ( DC  12 volts ) - DC IN/VS IN/VIDEO OUT BNC Connector

8.   (SSC-C374)

The composite video output  shall be 1.0  volt  peak to peak @ 75 Ohms,  sync negative via a BNC          connector.

9.   The signal to noise ratio shall be 48 db with AGC off.

C. MECHANICAL REQUIREMENTS

1.   The camera shall accept C-mount lenses.  Fine focus shall be accomplished via a recessed screw  for              image sensor back focus adjustment.

2.   To allow for flexibility of mounting, 1/4" x 20 mounting holes will be available on the top and bottom              of the camera chassis.

3.   The camera dimensions shall be 2 1/2"w x 2 1/4"h x 61/8"d  (64 x 57 x 155 mm) and                        weigh 1 lb. 7 oz. (660 grams).

D. ENVIRONMENTAL REQUIREMENTS

1.   The operating temperature shall be 14 degrees  F  to 122 degrees  F  (-10 degrees  C to +50 degrees C).  Operating humidity shall be 20 percent to 80 percent,  non-condensing.

2.   The camera will be suitable for indoor applications,  or outdoor applications with an approved              environmentally rated camera enclosure.

E. REFERENCES

1.   UL Listed 1409 - Low-Voltage Video Products Without Cathode-Ray-Tube Displays

2.   FCC Verified  Class A Digital Device

F. ACCESSORIES

1.   YS-W150 - Single camera adaptor:  Provides power/sync/video multiplexing via single coaxial cable               and two (2) isolated video outputs.

a. Video Input/DC Output :    BNC X1

b. Video Output:    			BNC X2

c. Sync Mode:    				Line Lock, Internal, or external

d  Sync Input:					BNC X1

e. Sync Output:    				BNC X1

f. Power Requirements:		AC 120 volts,  50/60 Hz

g. Power Consumption:    	15 watts

h. Maximum Cable Length:    1000 ft. using RG-59B/U

1500 ft. using RG-6A/U

2000 ft. using RG-11A/U

2.   YS-W250 - Four Camera Adapter:  Provides power/sync/video multiplexing via single cable for four              (4) cameras and two (2) isolated video outputs per camera.

a. Video Input/DC Output :    BNC X4

b. Video Output:    			BNC X8  (2 outputs per camera)

c. Sync Input:    				BNC X1

d. Sync Output y:    			BNC X1

e. Power Requirements:    	AC 120 volts,  50/60 Hz

f. Power Consumption:    		65 watts

g. Maximum Cable Length:    1000 ft. using RG-59B/U

1500 ft. using RG-6A/U

2000 ft. using RG-11A/U

(1996 Sony Electronics Inc.  All rights reserved.  Feature and specifications subject to change without notice.   Non-metric weights and measurements are approximate. SONY, HyperHAD, CCD Iris and Nothing Escapes Us are trademarks of Sony.