ARCHITECT & ENGINEER SPECIFICATIONS

SECTION  16780

VIDEO SURVEILLANCE SYSTEMS

SVT-L200

Real Time + +  VHS Time Lapse Recorder

PART  2 PRODUCTS

2.01	CCTV TIME LAPSE VIDEO RECORDER SPECIFICATIONS

A.	VIDEO - GENERAL REQUIREMENTS

1.	The VTR (video tape recorder) shall utilize standard VHS tape format.

2.	The recording system shall be Dual Azimuth,  4-Head helical  scanning system.

3.	The VTR shall feature three (3) user programmable time lapse recording modes. The time modes 	shall be 8/24/40 hour with a T-160 tape.

4.	The recording field rates shall be 8 hr/60 fields/sec; 24 hr/20 fields/sec; 40 hr/12 fields/sec.

5.	The VTR shall feature a menu driven, on screen display for programming system functions and unit 	status.  This shall be possible with or without an active video input.

6.	There shall be a programmable, position selectable,  time/date generator which shall display month, 	day, year, hour, minute and second in a shadow character format.

7.	For unattended continuous recording the VTR shall feature an automatic repeat record setting.  This 	function shall be automatically overridden in the event of an alarm.

8.	Extended series recording shall be available by cascading multiple units together via series in and 	out terminals located on the rear panel.  As recording on one VTR is complete, the next unit is 	signaled to power up and recording is continued.

9.	To allow for automatic program changes the recorder shall feature  seven (7) day, eight (8) event 	internal timer capabilities. For connection to external devices there shall be a +12 volts. 5.7k Ohm 	terminal  output that follows timer activations.

10.	The VTR shall provide a dry contact input terminal to allow recording start and stop via external 	equipment or timers.

11.	The VTR shall have provisions to allow entry of up to 20 days, designated as non working days 	which shall follow the holiday record setting on the timer program.

12.	The VTR shall provide a record check function that when activated shall rewind the tape for 	approximately three (3) seconds and playback the tape for approximately two (2)  seconds.  The unit 	shall then return to its original record mode.

13.	The VTR shall be capable of  forward and reverse field by field play back in the Still Mode.

14.	The VTR shall be capable of RS-232C communication with external devices, such as a personal    	computer,  via the optional SVT-RS1A interface board.

15.	The VTR shall provide a  mini jack for connection of an external remote control device.

16.	The VTR shall feature automatic head cleaning.

17.	To protect against unauthorized use or accidental system changes the VTR  shall feature a 	programmable security lock feature.

B.	VIDEO - ELECTRICAL REQUIREMENTS

1.	The input voltage shall be AC 120 volts, 60 Hz.  Power consumption shall be 17 watts.

2.	The VTR shall have thirty (30) day power protection failure for time/date and record mode.

3.	The signal system shall be EIA / NTSC standard for color video signals.

4.	The VTR shall produce a minimum 350 horizontal lines resolution, monochrome and 300 horizontal 	lines resolution, color.

5.	To obtain optimum picture performance the VTR shall feature Adaptive Picture Control (APC)  	which automatically adjusts for the optimum video head bias based on the current condition of the 	tape and the video heads.

6.	The composite video input shall be 1.0 volt  peak to peak @ 75 Ohms, unbalanced via BNC 	connector.

7.	The VTR shall be capable of video signal loop through on power off mode, and E-E mode during 	normal power ON conditions.

8.	The composite video output shall be 1.0 volt  peak to peak @ 75 Ohms,  unbalanced via BNC 	connector.

9.	The signal to noise ratio shall be more than 42 dB (EP).

10.	The approximate recording intervals for each record mode, with T-160 tape, shall be - 8 hr/ 1/60 sec; 	24 hr/.05 sec; 40 hr/.083 sec.

11.	A +5V, 5.7 kOhm (active low) switch pulse output terminal shall be provided for interfacing with 	externally driven switchers, multiplexers or other devices.  Switch pulse output of the unit shall be 	field or frame selectable.  It shall be selectable for 1,2,3,4,5,10,30 or 60 frames(s)/Field(s).

12.	 A clock set input and output terminal shall be provided on the rear of the unit.  This shall allow 	multi-unit clock synchronization, which shall be updated once per day, specified to the hour by end 	user.

13.	The recorder shall feature stationary erase head configuration.

14.	The fast forward/ rewind time with a T-160 tape shall be less than five (5) minutes.

C.	AUDIO REQUIREMENTS

1.	Audio recording shall be available in the 8, 24, and 40 hour recording modes.

2.	The audio input  shall be -7.8dBs @ 47 kOhms via an Phono style connector.

3.	The audio output shall be -7.8dBs  @ 600 Ohms via an Phono style connector.

4.	The VTR shall provide a MIC input , -60dBs, 600 Ohm via a mini jack connector.

D.	ALARM REQUIREMENTS

1.	For alarm record mode activation from external devices the VTR shall provide a normally open, dry 	contact input via screw terminals.

2.	There shall be a +5  volts,  4.7 kOhms alarm output available via screw terminals for connection to 	external devices.  The alarm output shall follow alarm input activation, active low.

3.	Alarm recording speeds shall be 8 hour mode or No Change (NC).

4.	The VTR shall be fitted with a built-in buzzer which shall be activated during alarm recording or end 	of tape. This buzzer shall be capable of being manually activated/deactivated.

5.	The VTR shall have switch selectable alarm duration speeds of twenty (20) seconds, one (1) minute, 	or follow the alarm activation period.

6.	An on-screen alarm recall log shall display the eight (8) alarms by alarm count, month, day and time 	of occurrence, plus a running count of up to 999 alarm activation's.

7.	To audit and select alarm activations for viewing,  the first five seconds of each alarm activation may 	be viewed via the alarm scan feature.

8.	 A warning out signal shall be provided in the event recording is interrupted due to tape jam.

9.	For signaling the end of the video tape a screw terminal output, +5 volts, 4.7 kOhm signal shall be 	provided, active low.  The alarm buzzer shall also activate.

E.	MECHANICAL REQUIREMENTS

1.	For  rack mount accessibility  the VTR shall feature front panel tape loading.

2.	The recorder dimensions shall be 16 5/8"w x 4"h x 13 3/4"d  ( 420 x 100 x 349 mm ) and weigh 12 	lb.  9 oz.   (5.8 kg)

3.	The VTR  shall be capable of work station surface mounting or EIA standard 19" rack mounting 	with optional rack mount assembly.

F.	ENVIRONMENTAL REQUIREMENTS

1.	The operating temperature shall be 41O F  to 104O F  (5O c to +40OC).  Operating humidity shall be 	35 percent to 80 percent,  non-condensing.

2.	The recorder will be suitable for indoor applications.  Proper ventilation and filtering shall be 	required to maintain operating temperature and air quality  when mounted in  equipment cabinets or  	other confined areas.

G.	REFERENCES

1.	UL Listed 1409 - Low-Voltage Video Products Without Cathode-Ray-Tube Displays

2.	CSA Listed C22.2 # 1

3.	FCC Verified, Class A Digital Device

H.	ACCESSORIES

1.	Optional

a.	SMB-5000 Rack Mount Kit - 3 units high (5.25")

b.	SVT-RS1A - RS-232C Interface Board

c.	T-160VE - 160 minute VHS Tape

(c) 1996 Sony Electronics Inc.  All rights reserved.  Feature and specifications subject to change without notice.  Non-metric weights and measurements are approximate. SONY, Remote Commander, WatchCorder,  Hi8, Rotary Flying Erase and Nothing Escapes Us are trademarks of Sony.