ARCHITECTS & ENGINEERS SPECIFICATIONS

SECTION 16780

VIDEO SURVIELANCE  SYSTEMS

YS-SX310 - 10 Channel Simplex Multiplexer - Color

YS-SX210 - 10 Channel Simplex Multiplexer - Monochrome

PART	2	PRODUCTS

2.01	CCTV SIGNAL MANAGMENT SYSTEM SPECIFICATIONS - MULTIPLEXERS

A.	VIDEO - GENERAL REQUIREMENTS

1.	The multiplexer shall provide time division multiplex field recording for up to ten (10) 	synchronous or asynchronous video inputs.

2.	System operating parameters shall be user programmable available through on screen menu 	selections.

3.	Record switching speeds shall be user programmable.  In the SP or switch signal mode unit  shall 	be set to 1 field per channel.  In EP mode the field recording rate shall be menu selectable 1 or 3 		fields per channel.

4.	The multiplexer shall provide an effective pixel rating of 720 x 228 (Y), 360 x 228 (chroma) 	with a horizontal resolution of 360 TV lines.

5.	To facilitate programming of  recording parameters on a video recorder,  the multiplexer shall be 	capable of viewing the  programming screen of the connected VTR through the multiplexer 	during system setup, without having to change physical video cable connections.

6.	The multiplexer shall provide Simplex  Operation with the following functions:

a.	Simultaneous Encode/Record and Live/Full or Sequence viewing.

b.	Live Viewing on Multiscreen, Sequential or Full screen.

c.	Decode/Playback of Multiscreen, Sequential or Full screen viewing.

7.	Monitor  viewing options in Live and Playback mode shall be:

a.	Full Screen

b.	Automatic Sequencing

1.	Full Screen

2.	Quad Mode

c.	Multiscreen

1.	Quad

2.	7 view

3.	10 view

8.	Monitor viewing during Encode/Record mode shall be Full screen or Sequencing.

9.	Sequential switching shall be available in Quad and Full screen modes.  Global sequence dwell 	timing 	shall be user programmable from 0.5 to 30 seconds.

10.	The multiplexer shall provide Freeze/Still picture function in both Live and Playback modes.  	To 	indicate the still feature is activated the character “S” shall replace the camera number.

11.	The unit shall provide a two times (2X) electronic zoom feature in both Live and Playback, Full 	or Multiscreen modes.  The character “Z” shall display in place of the camera number when the 	zoom feature is enabled.  The zoom and freeze/still features may be used simultaneously, in 	which case the camera number shall flash the characters “ZS”

12.	The multiplexer shall provide Time/Date generation and up to eight (8) alpha-numeric character 	titling per video input channel.

B.	VIDEO - ELECTRICAL REQUIREMENTS

1.	The input voltage shall be AC 120 volts, Hz.  Power consumption shall be less than 22 watts.

2. 	(YS-SX310)

The multiplexer shall process both EIA standard monochrome and NTSC standard color signals.  	The unit shall allow for any combination of monochrome and color video inputs.

(YS-SX210)

The multiplexer shall process EIA standard monochrome signals.

3.	The unit shall provide ten (10) composite video input channels, 1.0 volt peak to peak @ 75 	Ohms, sync negative via BNC connectors.  Each video input shall be loop through via BNC 	connector.  Video Loop through shall be possible with or without power being switched on.

4.	There shall be VTR input and output terminals, 1.0 volt peak to peak @ 75 Ohms via BNC X 2.

5.	Monitor output shall be 1.0 volt peak to peak @ 75 Ohms via BNC connector.

6.	The multiplexer shall have remote control capabilities via the supplied D-Sub 25 pin connector.

7.	Time and program settings shall be protected from power failure for thirty days via internal 	lithium battery.

8. 	Field refresh shall be internal via on screen selection, or externally controlled through the switch 	input terminals.

C.	ALARM REQUIREMENTS

1.	The multiplexer shall provide one alarm input per video input.  Alarm activation shall be contact 	closure via D-Sub 25 pin connector .

2. 	Monitor Display:

a. 	During Encode/Record:  Alarm activation shall automatically switch to full screen view of he 		camera in alarm.  Multiple alarms shall be sequenced in order of occurrence.  The video input 		in alarm shall be designated with a flashing  “A” in the place of the camera number.

b.	During Live/Multiscreen Viewing: Alarm activation shall automatically switch to 10 				division multiscreen mode.  The video input in alarm shall be designated with a flashing  “A” 		in the place of the camera number.  The corresponding camera number button shall also flash 		on the front of the unit.  Selecting the button of the camera in alarm shall cause the monitor to 		display a full screen view of that camera.

3.	The multiplexer shall provide Video Loss Detection.  In the event of video signal loss to any 		video input, the unit shall automatically switch to the 10 screen mode.  The character “A” shall 	flash for thirty seconds in that camera position.

4.	The multiplexer shall provide an alarm warning buzzer and be switch selectable ON/OFF.

5.	An Alarm Memory shall store up to 100 alarm events with the time, date and camera number 	recorded for easy retrieval of alarm events.

6.	Alarm output to an external device shall be available via a DC5V, 5.7K Ohm, active low 	terminal connection.

D.	MECHANICAL

1. 	The multiplexer dimensions shall be 161/2”w x 2 1/8”h x 12 5/8”d (420 x 54 x 320mm) and weigh 	approximately 9 lb. 4 oz (4.2 kg)

2.	The multiplexer shall be one rack unit (1.75 inches) in height, with the feet removed.

3.	Rack mounting shall be achieved with the supplied rack ears.

E.	ENVIRONMENTAL  REQUIREMENTS

1.	The operating temperature shall be 32 degrees F to 113 degrees F (0 degrees C to 45 degrees C).  	Operating humidity shall be 10 to 70%, non-condensing .

2.	The multiplexer shall be suitable for desk top and rack mounting with proper ventilation.

F.	REFERENCES

1.	UL 2044, C-UL

2. 	FCC, IC  Class B